Improve Pipeline Leak Detection and Mitigation

Pacific Gas and Electric Company Natural Gas Pipeline Rupture and Fire
San Bruno, California
September 9, 2010

This is an excerpt from the full investigative report. This information does not include all the safety issues, findings, and recommendations issued in the report, but instead focuses on those that are directly related to the safety item. Read the complete report https://ntsb.gov/investigations/AccidentReports/Reports/PAR1101.pdf

What Happened

On September 9, 2010, a 30-inch-diameter segment of an intrastate natural gas transmission pipeline, known as Line 132, owned and operated by the Pacific Gas and Electric Company (PG&E), ruptured in a residential area in San Bruno, California. The rupture produced a crater about 72 feet long by 26 feet wide. The section of pipe that ruptured, which was about 28 feet long and weighed about 3,000 pounds, was found 100 feet south of the crater. PG&E estimated that 47.6 million standard cubic feet of natural gas was released. The released natural gas ignited, resulting in a fire that destroyed 38 homes and damaged 70. Eight people were killed, many were injured, and many more were evacuated from the area.

Why It Happened

Probable Cause:

The National Transportation Safety Board determined that the probable cause of the accident was PG&E’s (1) inadequate quality assurance and quality control in 1956 during its Line 132 relocation project, which allowed the installation of a substandard and poorly welded pipe section with a visible seam weld flaw that, over time, grew to a critical size, causing the pipeline to rupture during a pressure increase stemming from poorly planned electrical work at the Milpitas Terminal; and (2) inadequate pipeline integrity management program, which failed to detect and repair or remove the defective pipe section.

Contributing to the accident were the California Public Utilities Commission’s (CPUC’s) and the US Department of Transportation’s exemptions of existing pipelines from the regulatory requirement for pressure testing, which likely would have detected the installation defects. Also contributing to the accident was the CPUC’s failure to detect the inadequacies of PG&E’s pipeline integrity management program. Contributing to the severity of the accident were the lack of either automatic shutoff valves or remote control valves on the line and PG&E’s flawed emergency response procedures and delay in isolating the rupture to stop the flow of gas.

Building Explosion and Fire

Silver Spring, MD

August 10, 2016

This is an excerpt from the full investigative report. This information does not include all the safety issues, findings, and recommendations issued in the report, but instead focuses on those that are directly related to the safety item. Read the complete report https://ntsb.gov/investigations/AccidentReports/Reports/PAR1901.pdf

What Happened

On August 10, 2016, a 14-unit apartment building in the Flower Branch apartment complex in Silver Spring, Maryland, partially collapsed due to a natural gas-fueled explosion and fire. The explosion and fire also heavily damaged an adjacent apartment building. As a result of this accident, 7 residents died, 65 residents were transported to the hospital, and 3 firefighters were treated and released from the hospital.

Prior to the accident, several residents of both apartment buildings reported to investigators that they smelled gas in the weeks and months leading up to the explosion. Two mercury service regulators and their associated piping were installed in all 26 buildings of the Flower Branch apartment complex between 1955 and 1956. Access to the meter room, located in the building’s basement, was restricted, and the room had only two windows: one enclosed with glass and the other covered with a piece of wood with two small holes for ventilation.

Why It Happened

Probable Cause:

The probable cause of the explosion was the failure of an indoor mercury service regulator with an unconnected vent line that allowed natural gas into the meter room, where it accumulated and ignited from an unknown ignition source. Contributing to the accident was the location of the mercury service regulators, which delayed or prevented leaks from being detected by odor.

Atmos Energy Corporation Natural Gas-Fueled Explosion

Dallas, Texas

February 23, 2018

This is an excerpt from the full investigative report. This information does not include all the safety issues, findings, and recommendations issued in the report, but instead focuses on those that are directly related to the safety item. Read the complete report https://www.ntsb.gov/investigations/AccidentReports/Reports/PAR2101.pdf

What Happened

On February 23, 2018, at 6:38 a.m. local time, a natural-gas–fueled explosion occurred at a home in Dallas, Texas. The residence sustained major structural damage, but when first responders arrived on scene at 6:44 a.m., they observed no smoke or fire. Four family members were injured, and one was killed in the explosion. Following the explosion, National Transportation Safety Board investigators located a through-wall crack in the 71-year-old natural gas main that served the residence. In the 2 days before this explosion, two gas-related incidents occurred on the same block at houses that were served by the same natural gas main, each resulting in significant structural damage and burn injuries to one occupant.

Why It Happened

Probable Cause:

The National Transportation Safety Board determined that the probable cause of this explosion was the ignition of an accumulation of natural gas that leaked from the gas main, which was damaged during a sewer replacement project 23 years earlier. The damaged gas main was undetected by Atmos Energy Corporation’s investigation of two related natural gas incidents on the 2 days prior to the explosion. Contributing to the explosion was Atmos Energy Corporation’s insufficient wet weather leak investigation procedures. Contributing to the severity of the explosion was Atmos Energy Corporation’s inaction to isolate the affected main and evacuate the houses. Contributing to the degradation of the pipeline system was Atmos Energy Corporation’s inadequate integrity management program.